## Figure 1
Figure 1: Average daily system consumption for Darwin-Katherine by month, 2017-18 to 2019‑20
Month | 2017-18 | 2018-19 | 2019-20 | 2019-20 Max | 2019-20 Min
July | 3.98 | 3.7 | 3.27 | 5.29 | 2.42
August | 4.04 | 3.77 | 3.45 | 5.29 | 2.42
September | 4.59 | 4.32 | 3.75 | 5.29 | 2.42
October | 5.17 | 4.79 | 4.55 | 5.29 | 2.42
November | 4.96 | 4.86 | 4.84 | 5.29 | 2.42
December | 4.88 | 4.85 | 4.8 | 5.29 | 2.42
January | 4.41 | 4.45 | 4.51 | 5.29 | 2.42
February | 4.51 | 4.75 | 4.75 | 5.29 | 2.42
March | 4.59 | 4.69 | 4.45 | 5.29 | 2.42
April | 4.62 | 4.26 | 4.21 | 5.29 | 2.42
May | 3.87 | 3.98 | 3.45 | 5.29 | 2.42
June | 3.64 | 3.31 | 3.33 | 5.29 | 2.42

## Figure 2
Figure 2: Historical and forecast annual system consumption for Darwin-Katherine, 2015‑16 to 2029-30
Year | Actual | Forecat
2013-14 | 1617.3493
2014-15 | 1622.9916
2015-16 | 1707.0411
2016-17 | 1639.7655
2017-18 | 1620.2589
2018-19 | 1573.0458
2019-20 | 1505.2724
2020-21 |  | 1503.218
2021-22 |  | 1501.6196
2022-23 |  | 1499.9801
2023-24 |  | 1499.7177
2024-25 |  | 1500.7547
2025-26 |  | 1503.0125
2026-27 |  | 1511.812
2027-28 |  | 1521.8435
2028-29 |  | 1533.0415
2029-30 |  | 1545.3455

## Figure 3
Figure 3: Historical and forecast distributed PV-installed capacity for Darwin-Katherine, 2016-17 to 2029-30
CATEGORY | Residential
Year | Forecast - residential | Actual - residential
2016-17 |  | 20.029
2017-18 |  | 29.434
2018-19 |  | 42.15
2019-20 |  | 59.044
2020-21 | 64.8163
2021-22 | 76.581
2022-23 | 88.5318
2023-24 | 99.6573
2024-25 | 110.0151
2025-26 | 119.6636
2026-27 | 128.6598
2027-28 | 137.0583
2028-29 | 144.9104
2029-30 | 152.2644
CATEGORY | Commercial
Year | Forecast - commerical | Actual - commercial
2016-17 |  | 12.5777
2017-18 |  | 15.2779
2018-19 |  | 17.2832
2019-20 |  | 18.8744
2020-21 | 20.3042
2021-22 | 21.7341
2022-23 | 23.1639
2023-24 | 24.5937
2024-25 | 26.0236
2025-26 | 27.4534
2026-27 | 28.8833
2027-28 | 30.3131
2028-29 | 31.7429
2029-30 | 33.1728

## Figure 4
Figure 4: Historical and forecast annual consumption met by generation types, for Darwin-Katherine, 2015-16 to 2029-30
Year | Thermal generation | Large-scale solar PV | Residential and commercial solar PV | Forecast system consumption | Actual system consumption | Total energy consumed (underlying) | In 2029-30 the percentage of (Large-scale PV + residential + commerical PV)/Total energy consumed
2015-16 | 1707.0411 | 0 | 21.9278 |  | 1707.0411 | 1728.9689 | 23.46%
2016-17 | 1639.7655 | 0 | 36.7302 |  | 1639.7655 | 1676.4957
2017-18 | 1620.2589 | 0 | 55.7754 |  | 1620.2589 | 1676.0343
2018-19 | 1573.0458 | 0 | 75.3503 |  | 1573.0458 | 1648.3961
2019-20 | 1505.2724 | 0 | 99.0211 |  | 1505.2724 | 1604.2935
2020-21 | 1449.55 | 53.668 | 119.1304 | 1503.218 |  | 1622.3484
2021-22 | 1357.8256 | 143.7941 | 137.5968 | 1501.6196 |  | 1639.2164
2022-23 | 1334.3204 | 165.6597 | 156.3236 | 1499.9801 |  | 1656.3037
2023-24 | 1333.1938 | 166.5239 | 173.8954 | 1499.7177 |  | 1673.6131
2024-25 | 1335.3091 | 165.4457 | 190.3928 | 1500.7547 |  | 1691.1476
2025-26 | 1337.1137 | 165.8987 | 205.8975 | 1503.0125 |  | 1708.91
2026-27 | 1345.9653 | 165.8467 | 220.4893 | 1511.812 |  | 1732.3013
2027-28 | 1357.0078 | 164.8356 | 234.2445 | 1521.8435 |  | 1756.0879
2028-29 | 1369.6395 | 163.402 | 247.235 | 1533.0415 |  | 1780.2766
2029-30 | 1381.3625 | 163.9831 | 259.5284 | 1545.3455 |  | 1804.874

## Figure 5
Figure 5: Historical and forecast maximum system demand for Darwin-Katherine, season years (year ending 31 August) 2015-16 to 2029-30
Year | ACTUAL | POE10 | POE50 | POE90
2015-16 | 293.92
2016-17 | 289.1
2017-18 | 288.13
2018-19 | 286.99
2019-20 | 272.13
2020-21 |  | 286.5727 | 277.4001 | 270.2622
2021-22 |  | 287.3578 | 279.4423 | 272.6743
2022-23 |  | 289.6504 | 281.2565 | 274.3855
2023-24 |  | 291.4012 | 283.0135 | 276.2117
2024-25 |  | 292.46 | 284.411 | 277.5474
2025-26 |  | 295.3715 | 286.6954 | 279.3638
2026-27 |  | 298.9462 | 290.0998 | 283.0231
2027-28 |  | 302.867 | 293.7871 | 286.8218
2028-29 |  | 306.2862 | 297.6207 | 290.6286
2029-30 |  | 310.0655 | 300.6874 | 293.6742

## Figure 6
Figure 6: Historical and forecast minimum system demand for Darwin-Katherine, season years (year ending 31 August) 2015-16 to 2029-30
Year | ACTUAL | POE10 | POE50 | POE90
2015-16 | 95.62
2016-17 | 107.75
2017-18 | 97.51
2018-19 | 93.97
2019-20 | 67.67
2020-21 |  | 76.3919 | 71.8788 | 67.4854
2021-22 |  | 69.9472 | 65.6029 | 61.4527
2022-23 |  | 63.8942 | 59.7663 | 55.5521
2023-24 |  | 60.5481 | 55.336 | 50.7133
2024-25 |  | 55.3036 | 50.1478 | 45.1765
2025-26 |  | 50.5355 | 44.9407 | 39.845
2026-27 |  | 45.9923 | 40.3249 | 35.1574
2027-28 |  | 41.6433 | 36.4077 | 31.748
2028-29 |  | 39.7021 | 34.3923 | 29.1776
2029-30 |  | 37.7737 | 31.7946 | 26.26

## Figure 7
Figure 7: Daily load profiles for Darwin-Katherine, wet and dry seasons, 2019-20
Year | Time | Underlying Demand - Wet Season (max) | Underlying Demand - Dry Season (min) | System Demand - Wet Season (max) | System Demand - Dry Season (min)
2018-19 | 0:00 | 184.652 | 114.479 | 184.652 | 114.479
2018-19 | 0:30 | 175.93 | 111.226 | 175.93 | 111.226
2018-19 | 1:00 | 171.267 | 107.807 | 171.267 | 107.807
2018-19 | 1:30 | 167.95 | 105.312 | 167.95 | 105.312
2018-19 | 2:00 | 165.461 | 103.788 | 165.461 | 103.788
2018-19 | 2:30 | 162.985 | 102.349 | 162.985 | 102.349
2018-19 | 3:00 | 161.615 | 101.418 | 161.615 | 101.418
2018-19 | 3:30 | 160.293 | 100.527 | 160.293 | 100.527
2018-19 | 4:00 | 159.619 | 101.049 | 159.619 | 101.049
2018-19 | 4:30 | 159.367 | 101.195 | 159.367 | 101.195
2018-19 | 5:00 | 160.085 | 101.621 | 160.029 | 101.621
2018-19 | 5:30 | 164.687 | 103.913 | 164.267 | 103.913
2018-19 | 6:00 | 170.4368 | 107.466 | 169.362 | 107.466
2018-19 | 6:30 | 184.8867 | 114.4608 | 183.052 | 114.342
2018-19 | 7:00 | 198.4572 | 120.0757 | 195.147 | 119.427
2018-19 | 7:30 | 214.6114 | 126.9898 | 207.995 | 124.271
2018-19 | 8:00 | 223.1991 | 132.8691 | 212.398 | 123.98
2018-19 | 8:30 | 231.2335 | 137.8934 | 215.957 | 123.161
2018-19 | 9:00 | 235.9374 | 140.4642 | 215.836 | 120.212
2018-19 | 9:30 | 237.856 | 141.1115 | 213.447 | 116.167
2018-19 | 10:00 | 242.1661 | 141.8944 | 213.842 | 112.938
2018-19 | 10:30 | 244.8114 | 141.5612 | 213.645 | 108.97
2018-19 | 11:00 | 249.009 | 141.4367 | 215.439 | 106.33
2018-19 | 11:30 | 254.5535 | 142.1179 | 219.488 | 104.987
2018-19 | 12:00 | 258.2444 | 143.8708 | 222.238 | 105.352
2018-19 | 12:30 | 261.3433 | 145.2064 | 224.66 | 106.133
2018-19 | 13:00 | 264.5432 | 146.8407 | 227.861 | 108.22
2018-19 | 13:30 | 267.4529 | 148.37 | 231.417 | 110.604
2018-19 | 14:00 | 270.2841 | 150.7509 | 235.6489 | 114.119
2018-19 | 14:30 | 272.214 | 153.5795 | 239.748 | 118.575
2018-19 | 15:00 | 274.8463 | 156.4575 | 244.735 | 123.92
2018-19 | 15:30 | 277.8583 | 159.3193 | 251.035 | 130.179
2018-19 | 16:00 | 281.2848 | 163.6719 | 258.232 | 138.151
2018-19 | 16:30 | 284.0985 | 166.0902 | 265.481 | 145.343
2018-19 | 17:00 | 278.5356 | 168.8383 | 265.09 | 152.327
2018-19 | 17:30 | 270.5295 | 169.2491 | 261.821 | 157.686
2018-19 | 18:00 | 264.9425 | 167.5662 | 260.292 | 161.369
2018-19 | 18:30 | 263.7397 | 166.7267 | 261.949 | 165.397
2018-19 | 19:00 | 262.8439 | 168.7594 | 262.397 | 168.737
2018-19 | 19:30 | 262.5983 | 164.273 | 262.397 | 164.273
2018-19 | 20:00 | 257.893 | 158.136 | 257.831 | 158.136
2018-19 | 20:30 | 250.6509 | 152.398 | 250.648 | 152.398
2018-19 | 21:00 | 242.904 | 147.076 | 242.904 | 147.076
2018-19 | 21:30 | 230.285 | 141.487 | 230.285 | 141.487
2018-19 | 22:00 | 221.05 | 135.635 | 221.05 | 135.635
2018-19 | 22:30 | 210.108 | 129.186 | 210.108 | 129.186
2018-19 | 23:00 | 200.528 | 123.805 | 200.528 | 123.805
2018-19 | 23:30 | 191.563 | 118.871 | 191.563 | 118.871

## Figure 8
Figure 8: Forecast reliability, Darwin-Katherine, 2020-21 to 2029-30
Year | No Maint. USE (%) | W_Maint. USE (%) | Remaining USE | USE attributable to Maintenance | Reliability standard
2020-21 | 1.693e-05% | 0.00163% | 1.693e-05% | 0.001613% | 0.002%
2021-22 | 3.473e-06% | 0.0001113% | 3.473e-06% | 0.0001078% | 0.002%
2022-23 | 1.362e-05% | 2.121e-05% | 1.362e-05% | 7.584e-06% | 0.002%
2023-24 | 1.167e-05% | 8.213e-06% | 8.213e-06% | 0% | 0.002%
2024-25 | 2.149e-06% | 2.951e-05% | 2.149e-06% | 2.737e-05% | 0.002%
2025-26 | 9.028e-07% | 6.013e-06% | 9.028e-07% | 5.11e-06% | 0.002%
2026-27 | 8.979e-05% | 0.0008227% | 8.979e-05% | 0.0007329% | 0.002%
2027-28 | 0.02875% | 0.1301% | 0.02875% | 0.1014% | 0.002%
2028-29 | 0.1982% | 0.4997% | 0.1982% | 0.3015% | 0.002%
2029-30 | 0.5003% | 0.9538% | 0.5003% | 0.4536% | 0.002%

## Figure 9
Figure 9: Forecast summer dispatchable thermal capacity and maximum system demand (POE10), Darwin-Katherine, 2020-21 to 2029-30
| 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
Dispatchable Thermal Capacity | 420.453 | 434.949 | 434.949 | 434.949 | 434.949 | 434.949 | 434.949 | 367.259 | 270.069 | 262.419
Maximum System Demand | 299.9575 | 301.0706 | 303.6689 | 305.6532 | 307.0432 | 310.1757 | 314.1627 | 318.3691 | 321.9416 | 325.9328

## Figure 10
Figure 10: Forecast effect of strict upkeep of system security requirements in USE (%), Darwin-Katherine, 2020-21 to 2029-30
Year | W_Maint. USE (%) | W_System security requirements USE (%) | Remaining USE | USE attributable to system security requirements | Reliability standard
2020-21 | 0.00163% | 0.0138% | 0.00163% | 0.01217% | 0.002%
2021-22 | 0.0001113% | 0.001382% | 0.0001113% | 0.00127% | 0.002%
2022-23 | 2.121e-05% | 0.0002886% | 2.121e-05% | 0.0002674% | 0.002%
2023-24 | 8.213e-06% | 0.000116% | 8.213e-06% | 0.0001077% | 0.002%
2024-25 | 2.951e-05% | 0.0002545% | 2.951e-05% | 0.000225% | 0.002%
2025-26 | 6.013e-06% | 0.0001246% | 6.013e-06% | 0.0001186% | 0.002%
2026-27 | 0.0008227% | 0.006054% | 0.0008227% | 0.005231% | 0.002%
2027-28 | 0.1301% | 0.4792% | 0.1301% | 0.3491% | 0.002%
2028-29 | 0.4997% | 1.516% | 0.4997% | 1.017% | 0.002%
2029-30 | 0.9538% | 2.645% | 0.9538% | 1.691% | 0.002%

## Figure 11
Figure 11: Forecast large-scale solar PV energy curtailment, Darwin-Katherine, 2020-21 to 2029-30
| Total Curtailment (MWh) |  |  |  | Total Curtailment (%)
Financial Year | Attributable to Oversupply | Attributable to reserve upkeep | Atributable to Inertia upkeep | Attributable to transmission constraint | Attributable to Oversupply | Attributable to reserve upkeep | Atributable to inertia upkeep | Attributable to transmission constraint
2020-21 | 0 | 4.9735 | 0 | 0 | 0% | 0.009267% | 0% | 0%
2021-22 | 0 | 105.2654 | 0 | 124.6265 | 0% | 0.07321% | 0% | 0.08667%
2022-23 | 0 | 249.4176 | 0 | 142.121 | 0% | 0.1506% | 0% | 0.08579%
2023-24 | 0 | 303.3849 | 0 | 2.5297 | 0% | 0.1822% | 0% | 0.001519%
2024-25 | 0 | 452.1379 | 0 | 2.8742 | 0% | 0.2733% | 0% | 0.001737%
2025-26 | 0 | 583.9027 | 0 | 1.4698 | 0% | 0.352% | 0% | 0.000886%
2026-27 | 0 | 807.3666 | 0 | 2.9849 | 0% | 0.4868% | 0% | 0.0018%
2027-28 | 0 | 1401.1129 | 0 | 341.1991 | 0% | 0.85% | 0% | 0.207%
2028-29 | 0 | 1804.1664 | 0 | 941.3577 | 0% | 1.104% | 0% | 0.5761%
2029-30 | 0 | 1420.6476 | 38.6749 | 986.3189 | 0% | 0.8663% | 0.02358% | 0.6015%

## Figure 12
Figure 12: Daily average system consumption for Alice Springs by month, 2017-18 to 2019-20
Month | 2017-18 | 2018-19 | 2019-20 | 2019-20 Max | 2019-20 Min
July | 0.53 | 0.59 | 0.55 | 0.9 | 0.37
August | 0.49 | 0.52 | 0.53 | 0.9 | 0.37
September | 0.49 | 0.47 | 0.47 | 0.9 | 0.37
October | 0.54 | 0.58 | 0.53 | 0.9 | 0.37
November | 0.6 | 0.61 | 0.58 | 0.9 | 0.37
December | 0.67 | 0.7 | 0.73 | 0.9 | 0.37
January | 0.74 | 0.83 | 0.74 | 0.9 | 0.37
February | 0.77 | 0.72 | 0.7 | 0.9 | 0.37
March | 0.59 | 0.67 | 0.57 | 0.9 | 0.37
April | 0.53 | 0.48 | 0.48 | 0.9 | 0.37
May | 0.5 | 0.48 | 0.47 | 0.9 | 0.37
June | 0.59 | 0.59 | 0.56 | 0.9 | 0.37

## Figure 13
Figure 13: Historical and forecast annual system consumption for Alice Springs, 2015-16 to 2029-30
Year | Actual | Forecast
2013-14 | 220.91
2014-15 | 221.9234
2015-16 | 218.9817
2016-17 | 216.9781
2017-18 | 213.9719
2018-19 | 220.6298
2019-20 | 210.2942
2020-21 |  | 211.5789
2021-22 |  | 248.2056
2022-23 |  | 248.0273
2023-24 |  | 247.8392
2024-25 |  | 247.6436
2025-26 |  | 247.5459
2026-27 |  | 247.6034
2027-28 |  | 247.7459
2028-29 |  | 247.967
2029-30 |  | 248.2608

## Figure 14
Figure 14 : Historical and forecast distributed PV-installed capacity, Alice Springs, 2016-17 to 2029-30
CATEGORY | Residential
Year | Forecast - residential | Actual - residential
2016-17 |  | 5.3231
2017-18 |  | 6.491
2018-19 |  | 7.3377
2019-20 |  | 9.1237
2020-21 | 10.4099
2021-22 | 11.9042
2022-23 | 13.4221
2023-24 | 14.9605
2024-25 | 16.5169
2025-26 | 17.9822
2026-27 | 19.3636
2027-28 | 20.6681
2028-29 | 21.9023
2029-30 | 23.0725
CATEGORY | Commercial
Year | Forecast - commerical | Actual - commercial
2016-17 |  | 2.36
2017-18 |  | 2.6088
2018-19 |  | 2.8648
2019-20 |  | 3.6755
2020-21 | 4.1725
2021-22 | 4.6694
2022-23 | 5.1664
2023-24 | 5.6633
2024-25 | 6.1602
2025-26 | 6.6572
2026-27 | 7.1541
2027-28 | 7.6511
2028-29 | 8.148
2029-30 | 8.645

## Figure 15
Figure 15: Historical and forecast annual consumption met by generation types, for Alice Springs, 2015-16 to 2029-30
Year | Thermal generation | Large-scale solar PV | Residential and commercial solar PV | Forecast system consumption | Actual system consumption | Total energy consumed (underlying)
2015-16 | 210.8201 | 8.1616 | 4.3969 |  | 218.9817 | 223.3786
2016-17 | 209.2072 | 7.7709 | 6.6708 |  | 216.9781 | 223.649
2017-18 | 205.4976 | 8.4743 | 8.9976 |  | 213.9719 | 222.9695
2018-19 | 212.2696 | 8.3602 | 10.7606 |  | 220.6298 | 231.3904
2019-20 | 201.092 | 9.2022 | 12.5953 |  | 210.2942 | 222.8894
2020-21 | 202.0954 | 9.4835 | 14.0534 | 211.5789 |  | 225.6324
2021-22 | 238.6654 | 9.5402 | 15.9724 | 248.2056 |  | 264.178
2022-23 | 238.4859 | 9.5415 | 17.9142 | 248.0273 |  | 265.9415
2023-24 | 238.3141 | 9.5251 | 19.8757 | 247.8392 |  | 267.7149
2024-25 | 238.1169 | 9.5267 | 21.8546 | 247.6436 |  | 269.4982
2025-26 | 238.0499 | 9.496 | 23.7457 | 247.5459 |  | 271.2915
2026-27 | 238.0954 | 9.5081 | 25.5559 | 247.6034 |  | 273.1593
2027-28 | 238.2282 | 9.5177 | 27.2919 | 247.7459 |  | 275.0379
2028-29 | 238.5221 | 9.4449 | 28.9603 | 247.967 |  | 276.9274
2029-30 | 238.791 | 9.4698 | 30.567 | 248.2608 |  | 278.8278

## Figure 16
Figure 16: Historical and forecast maximum system demand for Alice Springs, season years (year ending 31 August) 2015-16 to 2029-30
Year | ACTUAL | POE10 | POE50 | POE90
2015-16 | 53.11
2016-17 | 51.86
2017-18 | 52.67
2018-19 | 52.85
2019-20 | 50.85
2020-21 |  | 53.7861 | 51.1558 | 48.8644
2021-22 |  | 58.3579 | 55.4254 | 53.0965
2022-23 |  | 58.8894 | 55.5029 | 53.1881
2023-24 |  | 59.0086 | 55.6698 | 53.3616
2024-25 |  | 59.0318 | 55.7444 | 53.3942
2025-26 |  | 59.1167 | 55.8975 | 53.5193
2026-27 |  | 59.4757 | 56.3475 | 53.8292
2027-28 |  | 59.5933 | 56.504 | 54.0484
2028-29 |  | 60.3696 | 56.7178 | 54.415
2029-30 |  | 60.6719 | 56.9287 | 54.4825

## Figure 17
Figure 17: Annual historical and forecast minimum system demand for Alice Springs, season years (year ending 31 August) 2015-16 to 2029-30
Year | ACTUAL | POE10 | POE50 | POE90
2015-16 | 12.1
2016-17 | 12.72
2017-18 | 12.12
2018-19 | 11.02
2019-20 | 9.5
2020-21 |  | 9.2204 | 8.2814 | 7.2943
2021-22 |  | 12.4508 | 11.6306 | 10.6508
2022-23 |  | 11.8087 | 10.9283 | 9.9255
2023-24 |  | 11.0792 | 10.2139 | 9.246
2024-25 |  | 10.427 | 9.4864 | 8.3838
2025-26 |  | 9.8239 | 8.8607 | 7.8051
2026-27 |  | 9.0643 | 8.0695 | 7.0078
2027-28 |  | 8.5071 | 7.393 | 6.3201
2028-29 |  | 7.9782 | 6.7349 | 5.4947
2029-30 |  | 7.4049 | 6.2493 | 5.0836

## Figure 18
Figure 18: Daily load profile for Alice Springs, summer and shoulder, 2019-20
Year | Time | Underlying Demand - Summer (max) | Underlying Demand - Shoulder (min) | System Demand - Summer (max) | System Demand - Shoulder (min)
2018-19 | 43466 | 30.215 | 16.2933 | 30.215 | 16.2933
2018-19 | 43466.0208 | 27.582 | 16.586 | 27.582 | 16.586
2018-19 | 43466.0417 | 26.635 | 16.129 | 26.635 | 16.129
2018-19 | 43466.0625 | 26.086 | 15.911 | 26.086 | 15.911
2018-19 | 43466.0833 | 25.28 | 15.612 | 25.28 | 15.612
2018-19 | 43466.1042 | 24.819 | 15.335 | 24.819 | 15.335
2018-19 | 43466.125 | 24.442 | 15.141 | 24.442 | 15.141
2018-19 | 43466.1458 | 24.052 | 15.116 | 24.052 | 15.116
2018-19 | 43466.1667 | 23.77 | 15.216 | 23.77 | 15.216
2018-19 | 43466.1875 | 23.437 | 15.256 | 23.437 | 15.256
2018-19 | 43466.2083 | 23.686 | 15.41 | 23.686 | 15.41
2018-19 | 43466.2292 | 23.907 | 15.809 | 23.907 | 15.809
2018-19 | 43466.25 | 24.538 | 16.542 | 24.538 | 16.542
2018-19 | 43466.2708 | 26.0897 | 17.2567 | 26.058 | 17.256
2018-19 | 43466.2917 | 28.0578 | 17.3108 | 27.756 | 17.236
2018-19 | 43466.3125 | 31.1643 | 18.1179 | 30.322 | 17.55
2018-19 | 43466.3333 | 33.3943 | 18.1696 | 31.919 | 16.824
2018-19 | 43466.3542 | 35.7362 | 18.5879 | 33.61 | 16.517
2018-19 | 43466.375 | 37.1872 | 18.4884 | 34.45 | 15.694
2018-19 | 43466.3958 | 38.4222 | 17.968 | 35.139 | 14.689
2018-19 | 43466.4167 | 39.6146 | 17.7096 | 35.855 | 13.782
2018-19 | 43466.4375 | 40.6395 | 17.3197 | 36.483 | 12.972
2018-19 | 43466.4583 | 41.8847 | 17.1538 | 37.444 | 12.433
2018-19 | 43466.4792 | 42.7969 | 16.9826 | 38.167 | 12.014
2018-19 | 43466.5 | 44.356 | 16.7642 | 39.62 | 11.687
2018-19 | 43466.5208 | 45.5451 | 17.2873 | 40.813 | 12.116
2018-19 | 43466.5417 | 46.4652 | 17.4002 | 42.08 | 12.222
2018-19 | 43466.5625 | 48.0754 | 17.4697 | 43.546 | 12.389
2018-19 | 43466.5833 | 47.7382 | 18.047 | 43.468 | 13.146
2018-19 | 43466.6042 | 49.9396 | 14.9157 | 46.085 | 10.482
2018-19 | 43466.625 | 48.5972 | 15.4097 | 45.489 | 11.357
2018-19 | 43466.6458 | 49.1276 | 16.6504 | 45.969 | 13.049
2018-19 | 43466.6667 | 49.8861 | 17.5231 | 46.92 | 14.455
2018-19 | 43466.6875 | 50.0666 | 18.8029 | 47.835 | 16.359
2018-19 | 43466.7083 | 48.7485 | 19.6019 | 47.06 | 17.879
2018-19 | 43466.7292 | 48.0146 | 20.6675 | 46.63 | 19.533
2018-19 | 43466.75 | 47.1068 | 21.4557 | 46.297 | 21.058
2018-19 | 43466.7708 | 46.1362 | 22.4306 | 45.737 | 22.407
2018-19 | 43466.7917 | 45.2946 | 22.64 | 45.209 | 22.64
2018-19 | 43466.8125 | 45.011 | 22.234 | 45.011 | 22.234
2018-19 | 43466.8333 | 44.469 | 22.532 | 44.469 | 22.532
2018-19 | 43466.8542 | 42.989 | 20.859 | 42.989 | 20.859
2018-19 | 43466.875 | 41.241 | 20.807 | 41.241 | 20.807
2018-19 | 43466.8958 | 38.986 | 20.738 | 38.986 | 20.738
2018-19 | 43466.9167 | 36.767 | 20.537 | 36.767 | 20.537
2018-19 | 43466.9375 | 34.74 | 19.085 | 34.74 | 19.085
2018-19 | 43466.9583 | 32.835 | 18.291 | 32.835 | 18.291
2018-19 | 43466.9792 | 31.294 | 17.634 | 31.294 | 17.634

## Figure 19
Figure 19: Forecast reliability, Alice Springs, 2020-21 to 2029-30
Year | No Maint. USE (%) | W_Maint. USE (%) | Remaining USE | USE attributable to Maintenance | Reliability standard
2020-21 | 0% | 0% | 0% | 0% | 0.002%
2021-22 | 0% | 1.884e-05% | 0% | 1.884e-05% | 0.002%
2022-23 | 0.0004391% | 0.0004292% | 0.0004292% | 0% | 0.002%
2023-24 | 0.0001346% | 0.0003367% | 0.0001346% | 0.0002021% | 0.002%
2024-25 | 7.641e-05% | 0.0002886% | 7.641e-05% | 0.0002122% | 0.002%
2025-26 | 0.0004836% | 0.0004792% | 0.0004792% | 0% | 0.002%
2026-27 | 0.0006502% | 0.0005979% | 0.0005979% | 0% | 0.002%
2027-28 | 0.0005952% | 0.000478% | 0.000478% | 0% | 0.002%
2028-29 | 0.0001715% | 0.0001122% | 0.0001122% | 0% | 0.002%
2029-30 | 0.000126% | 0.0002117% | 0.000126% | 8.57e-05% | 0.002%

## Figure 20
Figure 20: Forecast summer dispatchable thermal capacity and maximum demand (POE10), Alice Springs, 2020-21 to 2029-30
| 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
Dispatchable Thermal Capacity | 116.095 | 116.095 | 75.605 | 75.605 | 75.605 | 75.605 | 75.605 | 75.605 | 75.605 | 75.605
Maximum System Demand | 56.2396 | 60.8777 | 61.4379 | 61.5896 | 61.6331 | 61.7501 | 63.902 | 62.2848 | 63.0849 | 63.4021

## Figure 21
Figure 21: Forecast effect of strict upkeep of system security requirements in USE (%), Alice Springs, 2020-21 to 2029-30
Year | W_Maint. USE (%) | W_System security requirements USE (%) | Remaing USE | USE attributable to System security requirements | Reliability standard
2020-21 | 0% | 9.327e-05% | 0% | 9.327e-05% | 0.002%
2021-22 | 1.884e-05% | 0.000682% | 1.884e-05% | 0.0006631% | 0.002%
2022-23 | 0.0004292% | 0.01536% | 0.0004292% | 0.01493% | 0.002%
2023-24 | 0.0003367% | 0.02543% | 0.0003367% | 0.0251% | 0.002%
2024-25 | 0.0002886% | 0.02021% | 0.0002886% | 0.01992% | 0.002%
2025-26 | 0.0004792% | 0.0182% | 0.0004792% | 0.01772% | 0.002%
2026-27 | 0.0005979% | 0.02002% | 0.0005979% | 0.01942% | 0.002%
2027-28 | 0.000478% | 0.01453% | 0.000478% | 0.01405% | 0.002%
2028-29 | 0.0001122% | 0.01357% | 0.0001122% | 0.01346% | 0.002%
2029-30 | 0.0002117% | 0.01782% | 0.0002117% | 0.01761% | 0.002%

## Figure 22
Figure 22: Forecast large-scale solar PV energy curtailment, Alice Springs, 2020-21 to 2029-30
| Total Curtailment (MWh) |  |  | Total Curtailment (%)
Year | Attributable to Oversupply | Attributable to reserve upkeep | Atributable to Inertia upkeep | Attributable to Oversupply | Attributable to reserve upkeep | Atributable to Inertia upkeep
2020-21 | 0 | 316.5801 | 0 | 0% | 3.338% | 0%
2021-22 | 0 | 313.1362 | 0 | 0% | 3.282% | 0%
2022-23 | 0 | 312.8812 | 0 | 0% | 3.279% | 0%
2023-24 | 0 | 311.347 | 0 | 0% | 3.269% | 0%
2024-25 | 0 | 316.513 | 0 | 0% | 3.322% | 0%
2025-26 | 0 | 331.5105 | 0 | 0% | 3.491% | 0%
2026-27 | 0 | 343.8409 | 0 | 0% | 3.616% | 0%
2027-28 | 0 | 355.76 | 0 | 0% | 3.738% | 0%
2028-29 | 0 | 364.2723 | 0 | 0% | 3.857% | 0%
2029-30 | 0 | 387.1654 | 0 | 0% | 4.088% | 0%

## Figure 23
Figure 23: Average daily system consumption for Tennant Creek by month, 2017-18 to 2019-20
Month | 2017-18 | 2018-19 | 2019-20 | 2019-20 Max | 2019-20 Min
July | 0.06 | 0.06 | 0.06 | 0.12 | 0.049185
August | 0.06 | 0.05 | 0.06 | 0.12 | 0.049185
September | 0.07 | 0.06 | 0.07 | 0.12 | 0.049185
October | 0.09 | 0.09 | 0.09 | 0.12 | 0.049185
November | 0.09 | 0.1 | 0.1 | 0.12 | 0.049185
December | 0.1 | 0.11 | 0.11 | 0.12 | 0.049185
January | 0.09 | 0.12 | 0.11 | 0.12 | 0.049185
February | 0.1 | 0.11 | 0.1 | 0.12 | 0.049185
March | 0.09 | 0.1 | 0.09 | 0.12 | 0.049185
April | 0.08 | 0.07 | 0.08 | 0.12 | 0.049185
May | 0.06 | 0.06 | 0.06 | 0.12 | 0.049185
June | 0.06 | 0.07 | 0.06 | 0.12 | 0.049185

## Figure 24
Figure 24: Historical and forecast annual system consumption for Tennant Creek, 2015-16 to 2029-30
Year | Actual | Forecast
2013-14 | 29.8937
2014-15 | 29.1806
2015-16 | 29.9072
2016-17 | 29.0579
2017-18 | 28.7738
2018-19 | 30.4353
2019-20 | 29.5736
2020-21 |  | 31.4868
2021-22 |  | 33.5608
2022-23 |  | 35.6345
2023-24 |  | 35.6056
2024-25 |  | 35.5765
2025-26 |  | 35.5473
2026-27 |  | 35.5251
2027-28 |  | 35.5028
2028-29 |  | 35.4803
2029-30 |  | 35.4577

## Figure 25
Figure 25: Historical and forecast distributed PV capacity, Tennant Creek, 2016-17 to 2029-30
CATEGORY | Residential
Year | Forecast - residential | Actual - residential
2016-17 |  | 0.242
2017-18 |  | 0.247
2018-19 |  | 0.247
2019-20 |  | 0.296
2020-21 | 0.30778
2021-22 | 0.31978
2022-23 | 0.33197
2023-24 | 0.34432
2024-25 | 0.35682
2025-26 | 0.36945
2026-27 | 0.38219
2027-28 | 0.39505
2028-29 | 0.408
2029-30 | 0.42104
CATEGORY | Commercial
Row Labels | Forecast - commerical | Actual - commercial
2016-17 |  | 0.1263
2017-18 |  | 0.1263
2018-19 |  | 0.1263
2019-20 |  | 0.1263
2020-21 | 0.12896
2021-22 | 0.13163
2022-23 | 0.13429
2023-24 | 0.13696
2024-25 | 0.13962
2025-26 | 0.14228
2026-27 | 0.14495
2027-28 | 0.14761
2028-29 | 0.15028
2029-30 | 0.15294

## Figure 26
Figure 26: Historical and forecast consumption met by generation types for Tennant Creek, 2015-16 to 2029-30
Year | Thermal generation | Large-scale solar PV | Residential and commercial solar PV | Forecast system consumption | Actual system consumption | Total energy consumed (underlying)
2015-16 | 29.9072 | 0 | 0.41763 |  | 29.9072 | 30.3248
2016-17 | 29.0579 | 0 | 0.53372 |  | 29.0579 | 29.5916
2017-18 | 28.7738 | 0 | 0.57594 |  | 28.7738 | 29.3498
2018-19 | 30.4353 | 0 | 0.60779 |  | 30.4353 | 31.043
2019-20 | 29.5736 | 0 | 0.63061 |  | 29.5736 | 30.2042
2020-21 | 31.4868 | 0 | 0.67317 | 31.4868 |  | 32.16
2021-22 | 33.5608 | 0 | 0.69577 | 33.5608 |  | 34.2566
2022-23 | 35.6345 | 0 | 0.71867 | 35.6345 |  | 36.3532
2023-24 | 35.6056 | 0 | 0.74182 | 35.6056 |  | 36.3474
2024-25 | 35.5765 | 0 | 0.76519 | 35.5765 |  | 36.3417
2025-26 | 35.5473 | 0 | 0.78876 | 35.5473 |  | 36.336
2026-27 | 35.5251 | 0 | 0.81251 | 35.5251 |  | 36.3376
2027-28 | 35.5028 | 0 | 0.83643 | 35.5028 |  | 36.3392
2028-29 | 35.4803 | 0 | 0.8605 | 35.4803 |  | 36.3408
2029-30 | 35.4577 | 0 | 0.88471 | 35.4577 |  | 36.3424

## Figure 27
Figure 27: Historical and forecast maximum system demand for Tennant Creek, season years (year ending 31 August) 2015-16 to 2029-30
Year | ACTUAL | POE10 | POE50 | POE90
2015-16 | 6.8
2016-17 | 6.82
2017-18 | 6.77
2018-19 | 7.17
2019-20 | 6.85
2020-21 |  | 8.5805 | 8.1543 | 7.8181
2021-22 |  | 8.7857 | 8.3727 | 8.0649
2022-23 |  | 8.9707 | 8.5856 | 8.2753
2023-24 |  | 8.9429 | 8.5975 | 8.2742
2024-25 |  | 8.9491 | 8.5872 | 8.2512
2025-26 |  | 8.9582 | 8.5824 | 8.2501
2026-27 |  | 9.0031 | 8.5863 | 8.2542
2027-28 |  | 8.9825 | 8.5657 | 8.2436
2028-29 |  | 8.9481 | 8.5578 | 8.2421
2029-30 |  | 8.9706 | 8.5519 | 8.2084

## Figure 28
Figure 28: Historical and forecast minimum system demand for Tennant Creek, season years (year ending 31 August) 2015-16 to 2029-30
Year | ACTUAL | POE10 | POE50 | POE90
2015-16 | 1.77
2016-17 | 1.71
2017-18 | 1.51
2018-19 | 1.52
2019-20 | 1.7
2020-21 |  | 1.7719 | 1.6966 | 1.6044
2021-22 |  | 2.0136 | 1.9257 | 1.8296
2022-23 |  | 2.1266 | 2.0474 | 1.9534
2023-24 |  | 2.1295 | 2.0455 | 1.9557
2024-25 |  | 2.1225 | 2.0442 | 1.9502
2025-26 |  | 2.1145 | 2.034 | 1.9424
2026-27 |  | 2.1154 | 2.0238 | 1.9289
2027-28 |  | 2.0875 | 2.0056 | 1.9042
2028-29 |  | 2.0853 | 1.9994 | 1.9025
2029-30 |  | 2.0821 | 1.9957 | 1.898

## Figure 29
Figure 29: Daily load profile for Tennant Creek, summer and winter, 2019-20
Year | Time | Underlying Demand - Summer (max) | Underlying Demand - Winter (min) | System Demand - Summer (max) | System Demand - Winter (min)
2018-19 | 43466 | 4.145 | 2.0982 | 4.145 | 2.0982
2018-19 | 43466.0208 | 3.773 | 2.0609 | 3.773 | 2.0609
2018-19 | 43466.0417 | 3.679 | 2.0045 | 3.679 | 2.0045
2018-19 | 43466.0625 | 3.61 | 1.9564 | 3.61 | 1.9564
2018-19 | 43466.0833 | 3.53 | 1.9209 | 3.53 | 1.9209
2018-19 | 43466.1042 | 3.472 | 1.8945 | 3.472 | 1.8945
2018-19 | 43466.125 | 3.403 | 1.8464 | 3.403 | 1.8464
2018-19 | 43466.1458 | 3.365 | 1.8255 | 3.365 | 1.8255
2018-19 | 43466.1667 | 3.327 | 1.7864 | 3.327 | 1.7864
2018-19 | 43466.1875 | 3.297 | 1.7973 | 3.297 | 1.7973
2018-19 | 43466.2083 | 3.293 | 1.8173 | 3.293 | 1.8173
2018-19 | 43466.2292 | 3.386 | 1.94 | 3.386 | 1.94
2018-19 | 43466.25 | 3.374 | 2.0673 | 3.374 | 2.0673
2018-19 | 43466.2708 | 3.4772 | 2.2055 | 3.476 | 2.2055
2018-19 | 43466.2917 | 3.7333 | 2.3803 | 3.72 | 2.38
2018-19 | 43466.3125 | 4.1091 | 2.551 | 4.072 | 2.5355
2018-19 | 43466.3333 | 4.486 | 2.5537 | 4.418 | 2.4991
2018-19 | 43466.3542 | 4.8564 | 2.5878 | 4.762 | 2.4973
2018-19 | 43466.375 | 5.1118 | 2.5875 | 4.986 | 2.4636
2018-19 | 43466.3958 | 5.1756 | 2.5183 | 5.022 | 2.3655
2018-19 | 43466.4167 | 5.3821 | 2.4684 | 5.207 | 2.2909
2018-19 | 43466.4375 | 5.5562 | 2.4532 | 5.36 | 2.2555
2018-19 | 43466.4583 | 5.7215 | 2.4943 | 5.515 | 2.2809
2018-19 | 43466.4792 | 5.9305 | 2.5135 | 5.711 | 2.2882
2018-19 | 43466.5 | 6.1402 | 2.6013 | 5.913 | 2.3673
2018-19 | 43466.5208 | 6.3782 | 2.6295 | 6.148 | 2.3918
2018-19 | 43466.5417 | 6.4653 | 2.6366 | 6.236 | 2.3991
2018-19 | 43466.5625 | 6.5224 | 2.6072 | 6.295 | 2.3745
2018-19 | 43466.5833 | 6.6329 | 2.6309 | 6.4178 | 2.407
2018-19 | 43466.6042 | 6.6772 | 2.585 | 6.481 | 2.3691
2018-19 | 43466.625 | 6.6843 | 2.6604 | 6.494 | 2.46
2018-19 | 43466.6458 | 6.7427 | 2.6907 | 6.574 | 2.5109
2018-19 | 43466.6667 | 6.786 | 2.729 | 6.644 | 2.5727
2018-19 | 43466.6875 | 6.6481 | 2.7773 | 6.53 | 2.6491
2018-19 | 43466.7083 | 6.5788 | 2.7878 | 6.488 | 2.6909
2018-19 | 43466.7292 | 6.4151 | 2.8319 | 6.351 | 2.77
2018-19 | 43466.75 | 6.3263 | 2.8492 | 6.287 | 2.8255
2018-19 | 43466.7708 | 6.2487 | 2.9416 | 6.235 | 2.94
2018-19 | 43466.7917 | 6.0648 | 3.0955 | 6.064 | 3.0955
2018-19 | 43466.8125 | 6.018 | 3.0064 | 6.018 | 3.0064
2018-19 | 43466.8333 | 5.887 | 2.8973 | 5.887 | 2.8973
2018-19 | 43466.8542 | 5.622 | 2.8455 | 5.622 | 2.8455
2018-19 | 43466.875 | 5.424 | 2.7509 | 5.424 | 2.7509
2018-19 | 43466.8958 | 5.177 | 2.6336 | 5.177 | 2.6336
2018-19 | 43466.9167 | 4.931 | 2.5182 | 4.931 | 2.5182
2018-19 | 43466.9375 | 4.691 | 2.4 | 4.691 | 2.4
2018-19 | 43466.9583 | 4.503 | 2.3036 | 4.503 | 2.3036
2018-19 | 43466.9792 | 4.314 | 2.1873 | 4.314 | 2.1873

## Figure 30
Figure 30: Forecast summer dispatchable thermal capacity and maximum demand (POE10), Tennant Creek, 2020-21 to 2029-30
| 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
Dispatchable Thermal Capacity | 18.65 | 18.65 | 18.65 | 18.65 | 18.65 | 18.65 | 18.65 | 18.65 | 18.65 | 16.85
Maximum System Demand | 8.7135 | 8.9244 | 9.114 | 9.0909 | 9.1018 | 9.1157 | 9.1654 | 9.1497 | 9.1201 | 9.1475

## Figure 31
Figure 31: Forecast effect of strict upkeep of system security requirements in USE (%), Tennant Creek, 2021 to 2029-30
Year | W_Maint. USE (%) | W_System security requirements USE (%) | Remaining USE | USE attributable to System security requirements | Reliability standard
2020-21 | 2.54e-10% | 1.678e-09% | 2.54e-10% | 1.424e-09% | 0.002%
2021-22 | 3.883e-08% | 4.424e-08% | 3.883e-08% | 5.41e-09% | 0.002%
2022-23 | 0% | 0% | 0% | 0% | 0.002%
2023-24 | 4.065e-08% | 1.154e-08% | 4.065e-08% | 0% | 0.002%
2024-25 | 4.187e-08% | 0% | 4.187e-08% | 0% | 0.002%
2025-26 | 6.253e-09% | 0% | 6.253e-09% | 0% | 0.002%
2026-27 | 0% | 0% | 0% | 0% | 0.002%
2027-28 | 0% | 0% | 0% | 0% | 0.002%
2028-29 | 0% | 5.086e-06% | 0% | 5.086e-06% | 0.002%
2029-30 | 2.516e-06% | 5.311e-05% | 2.516e-06% | 5.06e-05% | 0.002%

## Figure 35
Figure 35: 132 kV transmission line constraint relative to inertia in the Darwin node
PWC Scenarios |  | Calculations
Total Line Rating | Inertia in Darwin | Inetia in Darwin | Line Rating RoCoF = 4 Hz/s | Line Rating RoCoF = 2.25 Hz/s
45 | 642.048 | 500 | 80 | 45
55 | 744.408 | 600 | 96 | 54
45 | 612.942 | 700 | 112 | 63
45 | 593.132 | 800 | 128 | 72
54 | 715.302 | 900 | 144 | 81
74 | 861.222 | 1000 | 160 | 90
79 | 943.772 | 1100 | 176 | 99
89 | 1026.322 | 1200 | 192 | 108
99 | 1105.697